## Slide 1
Fast Power Abort PC1
EE1 Open request
Fast Power Abort PC2
EE2 Open request
Interlock Key 1
24V PS AUX1
24V PS AUX2
Quench Status
Pol switch 1 position changed or lost
Interlock Key 2
24V PS AUX1
24V PS AUX2
Quench Status
Pol switch 2 position changed or lost
Fast Power Abort

## Slide 2
Flash Boxes
High voltage box
High current box
Lhe box
Power Permit 1 or Power permit 2
Power status ON 1 or Power status ON 2

## Slide 3
PC Permit
PC permit 1
PC permit 2
Interlock Key 1
24V PS Aux1
24V PS Aux2
Quench status
DAQ status
Lead1@4.2K or below
Lead2@4.2K or below
Interlock Key 2
24V PS Aux1
24V PS Aux2
Quench status
DAQ status
Lead3@4.2K or below
Lead3@4.2K or below
Pol switch 1 pos 1 or pos 2
PC1 power fail
PC1 connected
PC1 status on
EE1 pwr permit
EE1 remote
EE1 no error
EE1 switch closed
EE1 SPA
EE1 flow switch
Pol switch 2 pos 1 or pos 2 PC2 power fail
PC2 connected
PC2 status on
EE2 pwr permit
EE2 remote
EE2 no error
EE2 switch closed
EE2 SPA
EE2 flow switch
Info to read the temperature:
Lead1 – TT690
Lead2 – TT691
Lead3 – TT692
Lead4 – TT693

## Slide 4
Extra
Param:
Q_TO_CRYO_MIN_CUR
Option 1 to read the current: Use EPICS (MAG-RCH1: I_MEAS, MAG-RCH2: I_MEAS)
Option 2 to read the current: I can provide you 4 signal 0-10V equivalent to 0-1000A. These signals correspond to the current for the 4 modules of the 2 power converters (each power converter is composed of 2 modules of 1000A). To have the total current they have to be summed (signal 1 and 2 for PC1 and signal 3 and 4 for PC 2)
If you receive the quench signal (quench status), there is a fast power abort (slide1) and you inform the cryogenic to start the “recovery sequence”.
If you receive the quench signal but the current from the power converter is below the “Q_TO_CRYO_MIN_CUR” , there is a fast power abort (slide1) but you don’t send the signal to the cryo
Can you add on epics 2 boxes corresponding to the current PC1, current PC2
Info to read the current:
Power converter 1 – MAG-RCH1:I_MEAS
Power converter 2 – MAG-RCH2:I_MEAS
Buttons:
Reset EE1 Pulse 0_1_0: 500 ms
Close EE1 Pulse 0_1_0: 500 ms
Open request EE1 (inversed logic) Pulse 1_0_1: 500 ms
Reset EE1 Pulse 0_1_0: 500 ms
Close EE2 Pulse 0_1_0: 500 ms
Open request EE2 (inversed logic) Pulse 1_0_1: 500 ms
Change polarity switch motor direction: Pulse 0_1_0: 500 ms
Switch polarity for PC1: Pulse 0_1_0 for 5 s or until reaching end switch in the direction of movement
Switch polarity for PC2: Pulse 0_1_0 for 5 s or until reaching end switch in the direction of movement

## Slide 5
Polarity switch motor controller
Buttons:
Move motor 1 towards pos 1
Condition: sw1 pos1 closed (input signal high)
Move motor 1 towards pos 2
Condition: sw1 pos2 closed (input signal high)
Move motor 2 towards pos 1
Condition: sw2 pos1 closed (input signal high)
Move motor 2 towards pos 2
Condition: sw2 pos2 closed (input signal high)
General interlock: PC power off