## TRUTH TABLE
[5 empty] | 2019-11-24 | [5 empty] | TYPE OF TEST TO SELECT
TEST CONFIG. |  |  | Signal name | EPICS core name P=CstatV-MagLPS | Signal description | PLC IO |  | Signal type |  | Signal conditionning | Power Main Magnet | Description
[6 empty] | Position | Address
| Par. | 1 | GERSEMI_Q_TO_CRYO_MIN_CUR |  | Minimum current for quench detection on cryo side |  |  | Gersemi parameter | Real |  | xxx A | Will be used for quench sequences (If (GERSEMI_PC_CUR_1 and GERSEMI_PC_CUR_2) < GERSEMI_Q_TO_CRYO_MIN_CUR then it's not a quench )
INPUT VALUES TO BE CHECKED | 6 ANALOG INPUTS ETHERNET | 1 | GERSEMI_PC_CUR_1 |  | Sum Current of Power converters |  |  | AI | 0-10V |  | NA | Needed only in Gersemi PLC (EPICS PV)
|  | 2 | GERSEMI_PC_CUR_2 |  | Sum Current of Power converters |  |  | AI | 0-10V |  | NA | Needed only in Gersemi PLC (EPICS PV)
|  | 3 | GERSEMI_V_LEAD_1 |  | Lead 1 voltage |  |  | Ethernet | -10/+10 V |  | BETWEEN -0.1 AND 0.1V | Needed only in Gersemi PLC. There is no thermo-switch. The signal can be generated based on ET650
|  | 4 | GERSEMI_V_LEAD_2 |  | Lead 2 voltage |  |  | Ethernet | -10/+10 V |  | BETWEEN -0.1 AND 0.1V | Needed only in Gersemi PLC. There is no thermo-switch. The signal can be generated based on ET651
|  | 5 | GERSEMI_V_LEAD_3 |  | Lead 3 voltage |  |  | Ethernet | -10/+10 V |  | BETWEEN -0.1 AND 0.1V | Needed only in Gersemi PLC. There is no thermo-switch. The signal can be generated based on ET652
|  | 6 | GERSEMI_V_LEAD_4 |  | Lead 4 voltage |  |  | Ethernet | -10/+10 V |  | BETWEEN -0.1 AND 0.1V | Needed only in Gersemi PLC. There is no thermo-switch. The signal can be generated based on ET653
| 32 DIGITAL INPUTS | 1 | GERSEMI_NO_Q_DETECTED | $(P):QuenchStat | No quench detected (from safety matrix) |  | I1.6 | DI | 24V | CONTACT | 1 | Signal from the safety matrix
|  | 2 | GERSEMI_DAQ_OK | $(P):DAQ_OK | DAQ system OK |  | I1.7 | DI | 24V | 5V with relay | 1
|  | 3 | GERSEMI_EE_1_POWER_PERMIT | $(P):EE-1:PwrPerm | Energy extraction switches give power permit |  | I0.0 | DI | 24V | 5-50mA current loop | 1 = OK | what: EE system is ready for powering or removes power-permit away in case of problems -> results in SPA | how: contacts relays on Future board
|  | 4 | GERSEMI_EE_1_REMOTE | $(P):EE-1:Remote | Energy extraction switches are in remote |  | I0.1 | DI | 24V | 5-50mA current loop | 1 = Remote | what: indication if L/R switch is in 'Local' mode | how: 2nd set of contacts from L/R switch
|  | 5 | GERSEMI_EE_1_NO_ERROR_CL | $(P):EE-1:NoError | Energy extraction switches have no internal errors |  | I0.2 | DI | 24V | 5-50mA current loop | 1 = OK | what: no internal fault in switch | how: contacts from relays on FPA board
|  | 6 | GERSEMI_EE_1_CLOSED | $(P):EE-1:Closed | Energy extraction switches are closed |  | I0.3 | DI | 24V | 5-50mA current loop | 1 = Closed | what: indication that switch is really closed
|  | 7 | GERSEMI_EE_1_WARNING | $(P):EE-1:NoWarn | Energy extraction is in warning |  | I0.4 | DI | 24V | 5-50mA current loop | 1 = OK | what: warning that switch is in a bad state, warning only, no power permit | how: contacts relays on Future board
|  | 8 | GERSEMI_EE_1_PC_SPA_OK | $(P):EE-1:SPAstat | Energy extraction switches request the Slow power abort on power converters |  | I0.5 | DI | 24V | 5-50mA current loop | 1 = OK | what: warning that switch is in a bad state, Slow Power Abort | how: contacts relays on Future board
|  | 9 | GERSEMI_EE_2_POWER_PERMIT | $(P):EE-2:PwrPerm | Energy extraction switches give power permit |  | I2.0 | DI | 24V | 5-50mA current loop | 1 = OK | what: EE system is ready for powering or removes power-permit away in case of problems -> results in SPA | how: contacts relays on Future board
|  | 10 | GERSEMI_EE_2_REMOTE | $(P):EE-2:Remote | Energy extraction switches are in remote |  | I2.1 | DI | 24V | 5-50mA current loop | 1 = Remote | what: indication if L/R switch is in 'Local' mode | how: 2nd set of contacts from L/R switch
|  | 11 | GERSEMI_EE_2_NO_ERROR_CL | $(P):EE-2:NoError | Energy extraction switches have no internal errors |  | I2.2 | DI | 24V | 5-50mA current loop | 1 = OK | what: no internal fault in switch | how: contacts from relays on FPA board
|  | 12 | GERSEMI_EE_2_CLOSED | $(P):EE-2:Closed | Energy extraction switches are closed |  | I2.3 | DI | 24V | 5-50mA current loop | 1 = Closed | what: indication that switch is really closed
|  | 13 | GERSEMI_EE_2_WARNING | $(P):EE-2:NoWarn | Energy extraction is in warning |  | I2.4 | DI | 24V | 5-50mA current loop | 1 = OK | what: warning that switch is in a bad state, warning only, no power permit | how: contacts relays on Future board
|  | 14 | GERSEMI_EE_2_PC_SPA_OK | $(P):EE-2:SPAstat | Energy extraction switches request the Slow power abort on power converters |  | I2.5 | DI | 24V | 5-50mA current loop | 1 = OK | what: warning that switch is in a bad state, Slow Power Abort | how: contacts relays on Future board
|  | 15 | GERSEMI_PC_1_POWERING_FAILURE | $(P):PC-1:PwrFail | Power converter status (http://te-epc-lpc.web.cern.ch/te-epc-lpc/concepts/converters/principles/principles_interfaces.stm#skcmd) |  | I0.6 | DI | 24V | CONTACT | 1 | Open: A fault is detected on the Power Converter (or its Power Part initiated (IGBT dead, or water fault), or even the output current not correctly regulated - FGC initiated). 01-02: cc =0 Shorted: Converter is not in fault, being OFF or ON.
|  | 16 | GERSEMI_PC_1_CONNECT | $(P):PC-1:Connected | PC connect (http://te-epc-lpc.web.cern.ch/te-epc-lpc/concepts/converters/principles/principles_interfaces.stm#skcmd) |  | I0.7 | DI | 24V | CONTACT | 1 | The contact PC_CONNECT shall be always shorted by the Power Supply receiving connector. This signal is used by the Interlock System to know if the cable between the Power Supply and the Interlock System is connected.
|  | 17 | GERSEMI_PC_1_EXT_OUT | $(P):PC-1:sOn | Power converter status |  | I1.0 | DI | 24V | CONTACT | 1 | Open: PC off - Shorted: PC on
|  | 18 | GERSEMI_PC_2_POWERING_FAILURE | $(P):PC-2:PwrFail | Power converter status (http://te-epc-lpc.web.cern.ch/te-epc-lpc/concepts/converters/principles/principles_interfaces.stm#skcmd) |  | I2.6 | DI | 24V | CONTACT | 1 | Open: A fault is detected on the Power Converter (or its Power Part initiated (IGBT dead, or water fault), or even the output current not correctly regulated - FGC initiated). 01-02: cc =0 Shorted: Converter is not in fault, being OFF or ON.
|  | 19 | GERSEMI_PC_2_CONNECT | $(P):PC-2:Connected | PC connect (http://te-epc-lpc.web.cern.ch/te-epc-lpc/concepts/converters/principles/principles_interfaces.stm#skcmd) |  | I2.7 | DI | 24V | CONTACT | 1 | The contact PC_CONNECT shall be always shorted by the Power Supply receiving connector. This signal is used by the Interlock System to know if the cable between the Power Supply and the Interlock System is connected.
|  | 20 | GERSEMI_PC_2_EXT_OUT | $(P):PC-2:sOn | Power converter status |  | I3.0 | DI | 24V | CONTACT | 1 | Open: PC off - Shorted: PC on
|  | 21 | GERSEMI_DC24V_AUX2_OK | $(P):DC24V:Aux2 | 24V AUX PS2 OK |  | I3.6 | DI | 24V | CONTACT | 1
|  | 22 | GERSEMI_DC24V_AUX1_OK | $(P):DC24V:Aux1 | 24V AUX PS1 OK |  | I3.5 | DI | 24V | CONTACT | 1 | from 24V Gersemi'sPLC
|  | 23 | GERSEMI_KEY1 | $(P):Key1 | Interlock KEY1 |  | I1.5 | DI | 24V | CONTACT | 1 | 0 = EB pressed
|  | 24 | GERSEMI_KEY2 | $(P):Key2 | Interlock KEY2 |  | I3.7 | DI | 24V | CONTACT | 1 | 0 = parking position
|  | 25 | GERSEMI_EE_1_FS | $(P):EE-1:FS | Signal from the water flow switch |  | I1.1 | DI | 24V
|  | 26 | GERSEMI_EE_2_FS | $(P):EE-2:FS | Signal from the water flow switch |  | I3.1 | DI | 24V
|  | 27 | GERSEMI_POLSW_1_POS1 | $(P):PolSw-1:Pos1 | Signal from the polarity switch posidtion 1 |  | I1.2 | DI | 24V
|  | 28 | GERSEMI_POLSW_1_POS2 | $(P):PolSw-1:Pos2 | Signal from the polarity switch posidtion 2 |  | I1.3 | DI | 24V
|  | 29 | GERSEMI_POLSW_2_POS1 | $(P):PolSw-2:Pos1 | Signal from the polarity switch posidtion 1 |  | I3.2 | DI | 24V
|  | 30 | GERSEMI_POLSW_2_POS2 | $(P):PolSw-2:Pos2 | Signal from the polarity switch posidtion 2 |  | I3.3 | DI | 24V
31
32
| DI ETHERNET | 1 | GERSEMI_CRYO_19K | $(P):CRYO_1_9K | cryo ok at 1.9K |  |  | Ethernet | DI |  | 1 / NA
|  | 2 | GERSEMI_CRYO_45K | $(P):CRYO_4_5_K | cryo ok at 4.5K |  |  | Ethernet | DI |  | NA / 1
|  | 3 | GERSEMI_CRYO_LEADS | $(P):CRYO_LEADS_OK | cryo ok on lead level |  |  | Ethernet | DI |  | 1 | 0 not enough Lhe
|  | 4 | GERSEMI_LEAD_1_TEMP_OK | $(P):LEAD1:T_OK | Temp. of lead 1 below threshold (PC_1) |  |  | Ethernet | DI |  | 1 | Over the network from Gersemi PLC. There is no thermo-switch. The signal can be generated based on TT690
|  | 5 | GERSEMI_LEAD_2_TEMP_OK | $(P):LEAD2:T_OK | Temp. of lead 2 below threshold (PC_1) |  |  | Ethernet | DI |  | 1 | Over the network from Gersemi PLC. There is no thermo-switch. The signal can be generated based on TT691
|  | 6 | GERSEMI_LEAD_3_TEMP_OK | $(P):LEAD3:T_OK | Temp. of lead 3 below threshold (PC_2) |  |  | Ethernet | DI |  | 1 | Over the network from Gersemi PLC. There is no thermo-switch. The signal can be generated based on TT692
|  | 7 | GERSEMI_LEAD_4_TEMP_OK | $(P):LEAD4:T_OK | Temp. of lead 4 below threshold (PC_2) |  |  | Ethernet | DI |  | 1 | Over the network from Gersemi PLC. There is no thermo-switch. The signal can be generated based on TT693
|  | 8 | GERSEMI_LEAD_1_VOLT_OK | $(P):LEAD1:V_OK | Voltage drop on lead 1 below threshold (PC_1) |  |  | Ethernet | DI |  |  | Over the network from Gersemi PLC. The signal can be generated based on ET650
|  | 9 | GERSEMI_LEAD_2_VOLT_OK | $(P):LEAD2:V_OK | Voltage drop on lead 2 below threshold (PC_1) |  |  | Ethernet | DI |  |  | Over the network from Gersemi PLC. The signal can be generated based on ET651
|  | 10 | GERSEMI_LEAD_3_VOLT_OK | $(P):LEAD3:V_OK | Voltage drop on lead 3 below threshold (PC_2) |  |  | Ethernet | DI |  |  | Over the network from Gersemi PLC. The signal can be generated based on ET652
|  | 11 | GERSEMI_LEAD_4_VOLT_OK | $(P):LEAD4:V_OK | Voltage drop on lead 4 below threshold (PC_2) |  |  | Ethernet | DI |  |  | Over the network from Gersemi PLC. The signal can be generated based on ET653
12
13
14
15
16
OUTPUT SIGNALS | 32 DIGITAL OUTPUTS | 1 | REMOVED: GERSEMI_DIRECT_PA | $(P):PC:DirectPA | REMOVERD: Power converters direct power abort in series with the safety Matrix |  | Q1.0 | DO | 24V | CONTACT | 0 if (GERSEMI_PC_1_POWERING_FAILURE or GERSEMI_PC_2_POWERING_FAILURE)=0;
|  | 2 | GERSEMI_PLC_EE_1_OPEN_RQ |  | Energy extraction swith open request |  | Q0.0 | DO | 24V | 5-50mA current loop | NC | what: decision from PLC to drop PLCloop | how: LED from PLC_FPAloop optocoupler switches off
|  | 3 | GERSEMI_CLOSE_EE_1 (500ms positive pulse) | $(P):EE-1:CloseCmd | Close energy extraction switches |  | Q0.1 | DO | 24V | 5-50mA current loop | ACTION taken by OPERATOR (Pulse 0_1_0: 500 ms) | what: command to close the switch (if no fault) | how: LED from optocoupler receives short pulse
|  | 4 | GERSEMI_RESET_EE_1 (500ms positive pulse) | $(P):EE-1:RstCmd | Reset energy extraction switches |  | Q0.2 | DO | 24V | 5-50mA current loop | ACTION taken by OPERATOR (Pulse 0_1_0: 500 ms) | what: RE-ARM switch before closing | how: contacts relays on Future board
|  | 5 | GERSEMI_PLC_EE_2_OPEN_RQ |  | Energy extraction swith open request |  | Q2.0 | DO | 24V | 5-50mA current loop | NC | what: decision from PLC to drop PLCloop | how: LED from PLC_FPAloop optocoupler switches off
|  | 6 | GERSEMI_CLOSE_EE_2 (500ms positive pulse) | $(P):EE-2:CloseCmd | Close energy extraction switches |  | Q2.1 | DO | 24V | 5-50mA current loop | ACTION taken by OPERATOR (Pulse 0_1_0: 500 ms) | what: command to close the switch (if no fault) | how: LED from optocoupler receives short pulse
|  | 7 | GERSEMI_RESET_EE_2 (500ms positive pulse) | $(P):EE-2:RstCmd | Reset energy extraction switches |  | Q2.2 | DO | 24V | 5-50mA current loop | ACTION taken by OPERATOR (Pulse 0_1_0: 500 ms) | what: RE-ARM switch before closing | how: contacts relays on Future board
|  | 8 | GERSEMI_PC_1_PERMIT | $(P):PC-1:PERM | Power permit |  | Q0.3 | DO | 24V | CONTACT | 1 if all DI = (1 or OK) ; 0 if at least one DI = (0 or NOK) | The contact PC_PERMIT (Power Permit) is open if the Interlock System orders the Power Supply to switch off smoothly. The contact is otherwise closed.
|  | 9 | GERSEMI_PC_2_PERMIT | $(P):PC-2:PERM | Power permit |  | Q2.3 | DO | 24V | CONTACT | 1 if all DI = (1 or OK) ; 0 if at least one DI = (0 or NOK) | The contact PC_PERMIT (Power Permit) is open if the Interlock System orders the Power Supply to switch off smoothly. The contact is otherwise closed.
|  | 10 | GERSEMI_PC_1_EXT | $(P):PC-1:fastPA | Fast power abort |  | Q0.4 | DO | 24V | CONTACT | 0 when (GERSEMI_EB_OK or GERSEMI_CRYO_LEADS or GERSEMI_DC24V_AUX_OK or DC24V_PLC_OK) = 0 | open: the Power Supply shall switch off immediately.
|  | 11 | GERSEMI_PC_2_EXT | $(P):PC-2:fastPA | Fast power abort |  | Q2.4 | DO | 24V | CONTACT | 0 when (GERSEMI_EB_OK or GERSEMI_CRYO_LEADS or GERSEMI_DC24V_AUX_OK or DC24V_PLC_OK) = 0 | open: the Power Supply shall switch off immediately.
|  | 12 | GERSEMI_FLSHBX_HVOLT | $(P):CPU-FLSHBX_HV | Flashbox (indicating High Voltage) |  | Q1.1 | DO | 24V | 230VAC by a relay | 1 when (GERSEMI_PC_1_EXT_OUT or GERSEMI_PC_2_EXT_OUT) = 1 0 when(GERSEMI_PC_1_EXT_OUT and GERSEMI_PC_2_EXT_OUT) goes to 0
|  | 13 | GERSEMI_FLSHBX_HCUR | $(P):CPU-FLSHBX_HC | Flashbox (indicating High Current) |  | Q1.2 | DO | 24V | 230VAC by a relay | 1 when (GERSEMI_PC_1_EXT_OUT or GERSEMI_PC_2_EXT_OUT) = 1 0 when(GERSEMI_PC_1_EXT_OUT and GERSEMI_PC_2_EXT_OUT) goes to 0
|  | 14 | GERSEMI_FLSHBX_HE | $(P):CPU-FLSHBX_HE | Flashbox (indicating Risk of Helium) |  | Q1.3 | DO | 24V | 230VAC by a relay | 1 when (GERSEMI_PC_1_EXT_OUT or GERSEMI_PC_2_EXT_OUT) = 1 0 when(GERSEMI_PC_1_EXT_OUT and GERSEMI_PC_2_EXT_OUT) goes to 0
|  | 15 | POLSW_1_MTR_ON | $(P):PolSw-1:cmdMove | Motor 1 power on |  | Q0.5 | DO | 24V |  | 1 when switching polarity until (GERSEMI_POLSW_1_POS1 = 1 AND POLSW_DIR_POS1 = 1) OR (GERSEMI_POLSW_1_POS2 = 1 AND POLSW_DIR_POS2 = 1) AND NOT GERSEMI_PC_1_EXT_OUT | When logical 1 powers motor 1
|  | 16 | POLSW_2_MTR_ON | $(P):PolSw-2:cmdMove | Motor 2 power on |  | Q2.5 | DO | 24V |  | 1 when switching polarity until (GERSEMI_POLSW_2_POS1 = 1 AND POLSW_DIR_POS1 = 1) OR (GERSEMI_POLSW_2_POS2 = 1 AND POLSW_DIR_POS2 = 1) AND NOT GERSEMI_PC_2_EXT_OUT | When logical 1 powers motor 2
|  | 17 | POLSW_DIR_POS1 | $(P):PolSw:dirPos1 | Direction towards pos1 switch |  | Q3.0 | DO | 24V |  | 1 when requested polarity switch towards pos1 | When logical 1 motor moves towards pos1 switch (I1.2 for motor 1, I3.2 for motor 2)
|  | 18 | POLSW_DIR_POS2 | $(P):PolSw:dirPos2 | Direction towards pos2 switch |  | Q3.1 | DO | 24V |  | 1 when requested polarity switch towards pos2 | When logical 1 motor moves toeards pos2 switch (I1.3 for motor 1, I3.3 for motor 2)
19
20
21
22
23
24
25
26
27
28
29
30
31
32
[5 empty] | Color codes: | Implemented |  | Not implemented

## EE
| Signal name | Type | Cable per rack or total | From | To | Cable nr and connector | Wires | connector PC side | Signal type | Signal logic
1 | EE-remote | Status |  | Switch | PLCSE | A - Burndy 12 F | 1-2 | Burndy 12 male | Iloop 5-50mA from TE-MSC | 1 = Remote | what: indication if L/R switch is in 'Local' mode
how: 2nd set of contacts from L/R switch
2 | EE-closed-loop | Status |  | Switch | PLCSE | A - Burndy 12 F | 3-4 | Burndy 12 male | Iloop 5-50mA from TE-MSC | 1 = OK | what: no internal fault in switch
how: contacts from relays on FPA board
3 | Close-EE | Command |  | PLCSE | Switch | B - Burndy 8 F | 1-2 | Burndy 8 male | Iloop 5-50mA from TE-MSC | Pulse 0_1_0: 500 ms | what: command to close the switch (if no fault)
how: led from optocoupler receives short pulse
4 | EE-closed | Status |  | Switch | PLCSE | A - Burndy 12 F | 5-6 | Burndy 12 male | Iloop 5-50mA from TE-MSC | 1 = Closed | what: indication that switch is really closed
how:
5 | PLC-SwitchOpen-request (Open-EE) | Command/Alarm |  | PLCSE | Switch | B - Burndy 8 F | 3-4 | Burndy 8 male | Iloop 5-50mA from TE-MSC | Pulse 0_1_0: 500 ms | what: decision from PLC to drop PLCloop
how: led from PLC_FPAloop optocoupler switches off
6 | EE-PC_SPA-request (Open EE) | Alarm |  | Switch | PLCSE | A - Burndy 12 F | 7-8 | Burndy 12 male | Iloop 5-50mA from TE-MSC | 1 = OK | what: warning that switch is in a bad state, Slow Power Abort
how: contacts relays on Future board
7 | EE-warning | Alarm |  | Switch | PLCSE | A - Burndy 12 F | 9-10 | Burndy 12 male | Iloop 5-50mA from TE-MSC | 1 = OK | what: warning that switch is in a bad state, warning only, no power permit
how: contacts relays on Future board
8 | EE-RESET | Command |  | PLCSE | Switch | B - Burndy 8 F | 5-6 | Burndy 8 male | Iloop 5-50mA from TE-MSC | Pulse 0_1_0: 500 ms | what: RE-ARM switch before closing
how: contacts relays on Future board
8 | EE-Power-Permit | Status |  | Switch | PLCSE | A - Burndy 12 F | 11-12 | Burndy 12 male | Iloop 5-50mA from TE-MSC | 1 = OK | what: EE system is ready for powering or removes power-permit away in case of problems -> results in SPA
how: contacts relays on Future board
| Matrix de securite |  |  |  |  | C - Burndy 5 F | 1-2 | Burndy 5 male | 1+, 2- |  | Max Chamion Clerc (future Pascale)
| Fast Power Abort Loop | Alarm | [6 empty] | Iloop 5-50mA from TE-MSC | 1 = OK | One 4 wire cable cable from matrix. Arrive as female, polarity 1+, 2- (3, 4 spare)

## PC
|  | Signal name | Type | Cable per rack or total | From | To | Cable nr and connector | Wires | connector PC side | Signal type
SKINTLK | 1 | POWERING_FAILURE | Status |  | PC | PLC | D - Burndy 12 M | 1-2 | Burndy 12 male | Isolated contact | Open: A fault is detected on the Power Converter (or its Power Part initiated (IGBT dead, or water fault), or even the output current not correctly regulated - FGC initiated) Shorted: Converter is not in fault, being OFF or ON.
| 2 | [5 empty] | D - Burndy 12 M | 3-4 | Burndy 12 male |  | Not used
| 3 | PC_CONNECT | Status |  | PC | PLC | D - Burndy 12 M | 5-6 | Burndy 12 male | Isolated short | The contact PC_CONNECT shall be always shorted by the Power Supply receiving connector. This signal is used by the Interlock System to know if the cable between the Power Supply and the Interlock System is connected.
| 4 | PC_FAST_ABORT | Command |  | Safety matrix | PC | D - Burndy 12 M | 7-8 | Burndy 12 male | Isolated contact | This input is dedicated to Interlock System, to switch off the converter based on critical conditions (fast_abort case, quench of superconductive magnet). Since several requester can be chained, this safe fail (open contact = converter off) signal must be isolated (requester side).
| 5 | [5 empty] | D - Burndy 12 M | 9-10 | Burndy 12 male |  | Not connected
| 6 | PC_PERMIT | Alarm |  | PLC | PC | D - Burndy 12 M | 11-12 | Burndy 12 male | Isolated contact | The contact PC_PERMIT (Power Permit) is open if the Interlock System orders the Power Supply to switch off smoothly. The contact is otherwise closed.
SKEXT | 1 | EXTERNAL | Command |  | PLC | PC | D - Burndy 4 M | 1-2 | Burndy 4 male | Isolated contact | Open: the Power Supply shall switch off immediately.
| 2 | EXTERNAL_OUT | Status |  | PC | PLC | D - Burndy 4 M | 3-4 | Burndy 4 male | Isolated contact | Open: PC on Shorted: PC off